## A-Steam Power Stations
Report Date - 06 MARCH 2004
A - Steam Power Stations
Power Stations | Type Fuel | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load MW | Remarks
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6
Dibis | Natural Gas | 4 | 1 | 8 | [5 empty] | 8 | 24 | #2 boiler leak; #3 prog maint; #4 boiler leak
Baiji | Fuel Oil | 6 | 2 | 85 |  |  |  |  | 80 | 165 | 500 | #1 synch at 0058; #2 prog maint; #4 synch at 1707 stopped at 306 FDF; #5 forced outage
Daura | Fuel Oil | 4 | 1 |  |  | 65 |  |  |  | 65 | 180 | #4 prog maint; #5 & #6 rehab
South Baghdad | Fuel Oil | 6 | 3 |  |  | 25 |  | 30 | 30 | 85 | 200 | #1 & #2 prog maint; #4 boiler leak
Mussaibe | Crude and Fuel Oil | 4 | 2 | 200 |  | 210 |  |  |  | 410 | 860 | #2 prog maint; #4 prog maint
Nassirya | Crude | 4 | 4 | 130 | 115 | 140 | 125 |  |  | 510 | 600
Najebia | Natural Gas and Crude | 2 | 1 |  |  |  |  | 90 |  | 90 | 160 | #4 valve leak
Hartha | Natural Gas and Crude | 4 | 2 | 60 |  |  | 120 |  |  | 180 | 300 | #1 high furnace press
| Out of Service for Unscheduled Maintanence | [7 empty] | Total: | 1513 | 2824
Out of Service for Program Maintanence/Rehab
No activity
Not Performing at Peak Performance

## B- Gas_C-Power Stations
Report Date - 06 MARCH 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 1 | 90 | 125 | Gas Oil | #2 lub oil leak from bearing | Musil Dam Main | 4 | 4 | 570 | 600
Quds | 2 | 2 | 80 | 160 | Gas Oil | 25 trucks | Musil Dam reg | 4 | 3 | 26 | 60 | 1000
Mosil | 12 | 9 | 140 | 150 | 28 | #1 & #9 rotor defect; #12 generator fault | Musil Pumping | 2 | 1 | 110 | 0
Dibis | 3 | 2 | 90 | 30 | 32 | #4 rehab; #5 synch at 1607 | Haditha Dam | 6 | 4 | 160 | 160 | 450
Old Mulla | 12 | 5 | 75 | 128 | 540 | #1 acc gear; #2 servo; #5 prog maint; #12 needs rehab | Samarra | 3 | 3 | 55 | 55
New Mulla | 6 | 4 | 120 | 173 | 3.4 | #2 prog maint; #6 generator defect | Himrin | 2 | 2 | 50 | 21
Taji | 7 |  |  | 55 |  | #3 compressor; #4 stopped at 600 control card | Hindia | 4 | 4 | 6 | 5
M. Taji | 2 |  |  | 18 |  | #2 software | Kufa | 4 | 2 | 2 | 0
Daura | 4 |  |  | 30 |  | #2 prog maint; #3 needs rehab |  |  | Total | 979 | 896
Hilla | 4 | 2 | 25 | 64 | 37 | #1 cooling sys prob; #2 servo | System Generation |  | 74267 | MWh
Najaf | 3 | 2 | 80 | 129 | 35 | #2 stopped at 1705 vib | Syrian Line Generation |  | 1350 | MWh
Khor | 4 | 3 | 110 | 80 | Natural Gas | #2 prog maint | Turkey Line Generation |  | 1797 | MWh
Shuaiba | 2 | 1 | 6 | 20 | Natural Gas | #1 prog maint | Total Generation |  | 82841 | MWh
M. Shuaiba | 2 |  |  |  | Natural Gas | split with the refinery | System Peak Load |  | 3448 | MW
Petro | 4 |  |  | 0 | Natural Gas | #2 vib | Syria Peak Load |  | 53 | MW
M. Dibis | 4 | 3 | 9 | 24 | Natural Gas |  | Turkey Peak Load |  | 80 | MW
Mossil East | 5 | 3 | 15 | 0 | Gas Oil |  | Fixed Gen Peak Load |  | 266 | MW
Hmam/Zafranya | 7 | 1 | 2 |  | Gas Oil |  | Total Peak Load |  | 3847 | MW
Diesel |  |  | 40 |  | Gas Oil |  | Baghdad Load |  | 1400 | MW
|  | Total | 882 | 1186
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
Report Date - 06 MARCH 2004
Power transferred from North to Middle 850 MW.
Power transferred from South to Middle 250 MW.
GOVERNORATE | Peak Load MW | MWH | Average Load MW
Baghdad | 1400 | 27414 | 1142
Duhok | 80 | 1866 | 78
Naynawa | 280 | 8252 | 344
Tamim | 124 | 3260 | 136
Salah Aldeen | 200 | 4912 | 205
Anbar | 190 | 4429 | 185
Dyala | 75 | 2043 | 85
Babil | 100 | 2205 | 92
Kirbala | 115 | 2238 | 93
Najaf | 132 | 2548 | 106
Kadsya | 65 | 1387 | 58
Wasit | 90 | 2081 | 87
Muthana | 50 | 1350 | 56
Nasirya | 120 | 2720 | 116
Misan | 65 | 1436 | 60
Basra | 275 | 6350 | 265