## A-Steam Power Stations
Reporting Peak for 10 MARCH 2004 / Report Date - 11 MARCH 2004
A - Steam Power Stations
Power Stations | Type Fuel | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load MW | Remarks
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6
Dibis | Natural Gas | 4 | 1 | 8 | [5 empty] | 8 | 24 | #3 prog maint; #4 6.35 vacuum
Baiji | Fuel Oil | 6 | 3 | 85 |  |  | 85 |  | 90 | 260 | 500 | #2 & #3 prog maint; #5 forced outage
Daura | Fuel Oil | 4 | 1 |  |  | 70 |  |  |  | 70 | 180 | #4 prog maint; #5 & #6 rehab
South Baghdad | Fuel Oil | 6 | 2 |  |  |  | 30 |  | 30 | 60 | 200 | #1 & #2 prog maint; #3 gen diff; #4 19-24 synch; #5 stopped at 2300 boiler leakage
Mussaibe | Crude and Fuel Oil | 4 | 2 | 205 |  | 215 |  |  |  | 420 | 860 | #2 prog maint; #4 prog maint
Nassirya | Crude | 4 | 2 | 130 |  |  | 130 |  |  | 260 | 600 | #2 prog maint; #3 02.55 vacuum
Najebia | Natural Gas and Crude | 2 | 2 |  |  |  | 80 | 80 |  | 160 | 160 | #4 valve leak
Hartha | Natural Gas and Crude | 4 | 1 | 95 | [5 empty] | 95 | 300 | #4 boiler leak
| Out of Service for Unscheduled Maintanence | [7 empty] | Total: | 1333 | 2824
Out of Service for Program Maintanence/Rehab
No activity
Not Performing at Peak Performance

## B- Gas_C-Power Stations
Reporting Peak for 10 MARCH 2004 / Report Date - 11 MARCH 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 1 | 100 | 125 | Gas Oil | #1 gas oil; #2 lub oil system | Musil Dam Main | 4 | 4 | 610 | 600
Quds | 2 | 2 | 200 | 160 | Gas Oil | 21 trucks | Musil Dam reg | 4 | 3 | 24 | 60 | 1000
Mosil | 12 | 9 | 135 | 150 | 32 | #1 & #9 rotor defect; #11 H.P. | Musil Pumping | 2 | 2 | 110 | 0
Dibis | 3 | 2 | 60 | 30 | 30 | #4 rehab | Haditha Dam | 6 | 3 | 195 | 160 | 600
Old Mulla | 12 | 8 | 120 | 128 | 570 | #1 acc gear; #2 servo; #5 & #6 synch; #12 needs rehab | Samarra | 3 | 3 | 67 | 55 | 670
New Mulla | 6 | 4 | 135 | 173 | 310 | #2 prog maint; #6 generator defect | Himrin | 2 | 2 | 50 | 21 | 250
Taji | 7 |  |  | 55 |  | #3 compressor; #4 stopped at 600 control card N.G. press low; #7 needs rehab | Hindia | 4 | 4 | 6 | 5
M. Taji | 2 |  |  | 18 |  | #2 software | Kufa | 4 | 3 | 2 | 0
Daura | 4 |  |  | 30 |  | #2 prog maint; #3 needs rehab NG press low |  |  | Total | 1064 | 896
Hilla | 4 | 3 | 44 | 64 | 25 | #2 synch at 1640; #3 turbine blades, prog maint | System Generation |  | 78527 | MWh
Najaf | 3 | 3 | 100 | 129 | 21 | #2 vib | Syrian Line Generation |  | 1357 | MWh
Khor | 4 | 3 | 90 | 80 | Natural Gas | #4 gen prot #2 | Turkey Line Generation |  | 1582 | MWh
Shuaiba | 2 | 1 | 5 | 20 | Natural Gas | #1 prog maint | Total Generation |  | 86893 | MWh
M. Shuaiba | 2 |  |  |  | Natural Gas |  | System Peak Load |  | 3655 | MW
Petro | 4 | 1 | 10 | 0 | Natural Gas | #2 vib | Syria Peak Load |  | 60 | MW
M. Dibis | 4 | 3 | 9 | 24 | Natural Gas |  | Turkey Peak Load |  | 85 | MW
Mossil East | 5 | 2 | 10 | 0 | Gas Oil |  | Fixed Gen Peak Load |  | 266 | MW
Hmam/Zafranya | 7 | 1 | 2 |  | Gas Oil |  | Total Peak Load |  | 4066 | MW
Diesel |  |  | 54 |  | Gas Oil |  | Baghdad Load |  | 1380 | MW
|  | Total | 1074 | 1186
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
Reporting Peak for 10 MARCH 2004 / Report Date - 11 MARCH 2004
Power transferred from North to Middle 835 MW.
Power transferred from South to Middle 185 MW.
GOVERNORATE | Peak Load MW | MWH | Average Load MW
Baghdad | 1380 | 29250 | 1219
Duhok | 85 | 1948 | 81
Naynawa | 319 | 9501 | 396
Tamim | 255 | 5177 | 216
Salah Aldeen | 201 | 5110 | 213
Anbar | 210 | 4405 | 184
Dyala | 90 | 2411 | 100
Babil | 95 | 2394 | 100
Kirbala | 80 | 1991 | 83
Najaf | 97 | 2469 | 103
Kadsya | 60 | 1447 | 60
Wasit | 95 | 2176 | 91
Muthana | 60 | 1370 | 57
Nasirya | 125 | 2683 | 112
Misan | 60 | 1430 | 60
Basra | 300 | 6190 | 258