## A-Steam Power Stations
Reporting Peak for 02 APRIL 2004 / Report Date - 03 APRIL 2004
A - Steam Power Stations
Power Stations | Type Fuel | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load MW | Remarks
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6
Dibis | Natural Gas | 4 | 2 | 8 |  | 8 |  |  |  | 16 | 24 | #2 stopped at 1513 BL; #3 synch at 1137; #4 prog maint
Baiji | Fuel Oil | 6 | 2 |  |  |  | 80 |  | 80 | 160 | 500 | #1 prog maint; #2 synch at 1912, stopped at 225 low air flow; #3 prog maint; #5 forced outage; #6 synch at 739
Daura | Fuel Oil | 4 | [7 empty] | 0 | 180 | #3 prog maint; #4 prog maint; #5 & #6 rehab
South Baghdad | Fuel Oil | 6 | 2 |  |  |  |  | 30 | 30 | 60 | 200 | #1, #2, #3 prog maint; #4 synch at 458, stopped at 330 high furnace press; #5 synch at 515
Mussaibe | Crude and Fuel Oil | 4 | 2 | 200 |  | 210 |  |  |  | 410 | 860 | #2 & #4 prog maint
Nassirya | Crude | 4 | [7 empty] | 0 | 600 | #1 & #2 prog maint, shut down at 130 for 2 weeks
Najebia | Natural Gas and Crude | 2 | 2 |  |  |  | 90 | 90 |  | 180 | 160
Hartha | Natural Gas and Crude | 4 | 1 |  |  |  | 150 |  |  | 150 | 300 | #1 prog maint
| Out of Service for Unscheduled Maintanence | [7 empty] | Total: | 976 | 2824
Out of Service for Program Maintanence/Rehab
No activity
Not Performing at Peak Performance

## B- Gas_C-Power Stations
Reporting Peak for 02 APRIL 2004 / Report Date - 03 APRIL 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | 4 | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 2 | 180 | 125 | Gas Oil |  | Musil Dam Main | 4 | 4 | 610 | 600
M. Baiji | 8 | 4 | 96 |  | Gas Oil |  | Musil Dam reg | 4 | 4 | 46 | 60 | 1100
Quds | 2 | 2 | 200 | 160 | Gas Oil | 36 trucks | Musil Pumping | 2 | 1 | 112 | 0
Mosil | 12 | 8 | 120 | 150 | 33 | #1 rotor defect; #3 stopped at 1440 on 1/4 servo; #9 rotor defect; #11 prog maint | Haditha Dam | 6 | 4 | 200 | 160 | 850
Dibis | 3 | 1 | 27 | 30 | 32 | #4 rehab; #6 synch at 1120, stopped at 2002 vib | Samarra | 3 | 3 | 67 | 55 | 700
Old Mulla | 12 | 5 | 70 | 128 | 520 | #6 generator defect (sch at 15/5) | Himrin | 2 | 2 | 40 | 21 | 125
New Mulla | 6 | 5 | 160 | 173 | 3.2 | #2 stopped at 830 temp diff; #3 compressor; #55 stopped at 1200 oil leak; #6 prog maint; #7 needs rehab | Hindia | 4 | 2 | 3 | 5 | 60
Taji | 7 | 2 | 27 | 55 | 18 | #2 software | Kufa | 4 | 2 | 1 | 0
M. Taji | 2 | 1 | 8 | 18 | Gas Oil | #2 prog maint; #3 needs rehab; #4 synch at 1010 |  |  | Total | 1079 | 896
Daura | 4 | 2 | 45 | 30 | 17 |  | System Generation |  | 70530 | MWh
Hilla | 4 | 4 | 68 | 64 | 24 |  | Syrian Line Generation |  | 1350 | MWh
Najaf | 3 | 3 | 116 | 129 | 22 | #2 prog maint | Turkey Line Generation |  | 1864 | MWh
Khor | 4 | 3 | 115 | 80 | Natural Gas |  | Total Generation |  | 79171 | MWh
Shuaiba | 2 | 1 | 4 | 20 | Natural Gas |  | System Peak Load |  | 3500 | MW
M. Shuaiba | 2 |  |  |  | Natural Gas |  | Syria Peak Load |  | 57 | MW
Petro | 4 |  |  | 0 | Natural Gas |  | Turkey Peak Load |  | 80 | MW
M. Dibis | 4 | 2 | 6 | 24 | Natural Gas |  | Fixed Gen Peak Load |  | 266 | MW
Mossil East | 5 | 3 | 15 | 0 | Gas Oil |  | Total Peak Load |  | 3903 | MW
Hmam/Zafranya | 7 | 1 | 2 |  | Gas Oil |  | Baghdad Load |  | 1180 | MW
Diesel |  |  | 31 |  | Gas Oil
|  | Total | 1290 | 1186
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
Reporting Peak for 02 APRIL 2004 / Report Date - 03 APRIL 2004
Power transferred from North to Middle 1075 MW.
Power transferred from South to Middle 130 MW.
GOVERNORATE | Peak Load MW | MWH | Average Load MW | Demand Load MW
Baghdad | 1180 | 24696 | 1029 | 1292
Duhok | 80 | 1824 | 76 | 104
Naynawa | 380 | 7749 | 323 | 449
Tamim | 165 | 3302 | 138 | 181
Salah Aldeen | 210 | 4501 | 188 | 224
Anbar | 200 | 4222 | 176 | 212
Dyala | 100 | 2048 | 85 | 131
Babil | 115 | 2356 | 98 | 137
Kirbala | 95 | 2128 | 89 | 110
Najaf | 110 | 2444 | 102 | 131
Kadsya | 65 | 1471 | 61 | 84
Wasit | 95 | 2138 | 89 | 116
Muthana | 60 | 1385 | 58 | 77
Nasirya | 100 | 1799 | 75 | 114
Misan | 65 | 1496 | 62 | 85
Basra | 320 | 6754 | 28 | 281