## A-Steam Power Stations
Reporting Peak for 11 APRIL 2004 / Report Date - 12 APRIL 2004
A - Steam Power Stations
Power Stations | Type Fuel | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load MW | Remarks
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6
Dibis | Natural Gas | 4 | 2 | 8 |  | 8 |  |  |  | 16 | 24 | #2 boiler leakage; #4 prog maint
Baiji | Fuel Oil | 6 | 3 |  | 100 |  | 80 |  | 80 | 260 | 500 | #1, #3 prog maint; #5 forced outage; #6 synch at 2348
Daura | Fuel Oil | 4 | [7 empty] | 0 | 180 | #3, #4 prog maint; #5, #6 rehab
South Baghdad | Fuel Oil | 6 | 3 |  |  |  | 30 | 30 | 30 | 90 | 200 | #1, #2, #3 prog maint; #5 synch at 110 on 10/4
Mussaibe | Crude and Fuel Oil | 4 | 2 | 215 |  | 220 |  |  |  | 435 | 860 | #2, #4 prog maint
Nassirya | Crude | 4 | [7 empty] | 0 | 600 | #1, #2 prog maint-shutdown till 4/15
Najebia | Natural Gas and Crude | 2 | 2 |  |  |  | 70 | 75 |  | 145 | 160
Hartha | Natural Gas and Crude | 4 | 1 |  |  |  | 135 |  |  | 135 | 300 | #1 prog maint
| Out of Service for Unscheduled Maintanence | [7 empty] | Total: | 1081 | 2824
Out of Service for Program Maintanence/Rehab
No activity
Not Performing at Peak Performance

## B- Gas_C-Power Stations
Reporting Peak for 11 APRIL 2004 / Report Date - 12 APRIL 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 1 | 75 | 125 | Gas Oil | #1 diff press | Musil Dam Main | 4 | 4 | 610 | 600
M. Baiji | 8 |  |  |  | Gas Oil |  | Musil Dam reg | 4 | 4 | 48 | 60 | 900
Quds | 2 | 2 | 200 | 160 | Gas Oil | 29 trucks | Musil Pumping | 2 | 1 | 110 | 0
Mosil | 12 | 9 | 135 | 150 | 29 | #1 & #9 rotor defect; #11 prog maint | Haditha Dam | 6 | 4 | 200 | 160 | 600
Dibis | 3 | 2 | 45 | 30 | 32 | #4 rehab | Samarra | 3 | 3 | 54 | 55 | 630
Old Mulla | 12 | 6 | 85 | 128 | 540 | #1 acc gear; #3 synch at 1405; #5 prim prot.; #6 HET; #7 gen vib; #8 vib; #10 synch at 1156; #12 needs rehab | Himrin | 2 | 2 | 36 | 21 | 10
New Mulla | 6 | 5 | 154 | 173 | 3.3 | #3 compressor; #5 excit prob; #6 prog maint; #7 needs rehab | Hindia | 4 | 4 | 6 | 5 | 140
Taji | 7 | 4 | 56 | 55 | 18 | #2 software | Kufa | 4 | 2 | 1 | 0 | 30
M. Taji | 2 |  |  | 18 | Gas Oil | #3 needs rehab; #4 starting |  |  | Total | 1065 | 896
Daura | 4 | 2 | 35 | 30 | 17 | #5 test | System Generation |  | 68869 | MWh
Hilla | 4 | 4 | 66 | 64 | 26 |  | Syrian Line Generation |  | 1409 | MWh
Najaf | 3 | 3 | 130 | 129 | 25 | #1, #2 prog maint | Turkey Line Generation |  | 1939 | MWh
Khor | 4 | 2 | 50 | 80 | Natural Gas |  | Total Generation |  | 77644 | MWh
Shuaiba | 2 | 1 | 5 | 20 | Natural Gas |  | System Peak Load |  | 3297 | MW
M. Shuaiba | 2 |  |  |  | Natural Gas |  | Syria Peak Load |  | 60 | MW
Petro | 4 | 1 | 10 | 0 | Natural Gas |  | Turkey Peak Load |  | 80 | MW
M. Dibis | 4 | 3 | 9 | 24 | Natural Gas |  | Fixed Gen Peak Load |  | 266 | MW
Mossil East | 5 | 3 | 17 | 0 | Gas Oil |  | Total Peak Load |  | 3703 | MW
Hmam/Zafranya | 7 |  |  |  | Gas Oil |  | Baghdad Load |  | 1140 | MW
Diesel |  |  |  |  | Gas Oil
|  | Total | 1072 | 1186
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
Reporting Peak for 11 APRIL 2004 / Report Date - 12 APRIL 2004
Power transferred from North to Middle 840 MW.
Power transferred from South to Middle - 210 MW.
GOVERNORATE | Peak Load MW | MWH | Average Load MW | Demand Load MW
Baghdad | 1140 | 24138 | 1006 | 1329
Duhok | 80 | 1912 | 80 | 112
Naynawa | 340 | 7934 | 331 | 488
Tamim | 145 | 3148 | 131 | 181
Salah Aldeen | 210 | 4877 | 203 | 263
Anbar | 185 | 4192 | 175 | 240
Dyala | 80 | 1993 | 83 | 131
Babil | 100 | 2458 | 102 | 141
Kirbala | 115 | 2130 | 89 | 93
Najaf | 135 | 2498 | 104 | 116
Kadsya | 85 | 1967 | 82 | 117
Wasit | 75 | 1411 | 59 | 92
Muthana | 50 | 1414 | 59 | 88
Nasirya | 80 | 2032 | 85 | 128
Misan | 55 | 1602 | 67 | 87
Basra | 320 | 5933 | 247 | 247