## A-Steam Power Stations
Reporting Peak for 12 APRIL 2004 / Report Date - 13 APRIL 2004
A - Steam Power Stations
Power Stations | Type Fuel | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load MW | Remarks
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6
Dibis | Natural Gas | 4 | 2 | 8 |  | 8 |  |  |  | 16 | 24 | #2 boiler leakage; #4 prog maint
Baiji | Fuel Oil | 6 | 3 |  | 95 |  | 70 |  | 100 | 265 | 500 | #1, #3 prog maint; #5 forced outage
Daura | Fuel Oil | 4 | [7 empty] | 0 | 180 | #3, #4 prog maint; #5, #6 rehab
South Baghdad | Fuel Oil | 6 | 3 |  |  |  | 30 |  | 30 | 60 | 200 | #1, #2, #3 prog maint; #5 stopped at 1230 BL
Mussaibe | Crude and Fuel Oil | 4 | 2 | 205 |  | 220 |  |  |  | 425 | 860 | #2, #4 prog maint
Nassirya | Crude | 4 | [7 empty] | 0 | 600 | #1, #2 prog maint - shutdown till 4/15
Najebia | Natural Gas and Crude | 2 | 1 |  |  |  |  | 40 |  | 40 | 160 | Shut down at 1759 - #5 synch at 656
Hartha | Natural Gas and Crude | 4 | 1 |  |  |  | 165 |  |  | 165 | 300 | #1 prog maint
| Out of Service for Unscheduled Maintanence | [7 empty] | Total: | 971 | 2824
Out of Service for Program Maintanence/Rehab
No activity
Not Performing at Peak Performance

## B- Gas_C-Power Stations
Reporting Peak for 12 APRIL 2004 / Report Date - 13 APRIL 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 1 | 90 | 125 | Gas Oil | #1 diff press | Musil Dam Main | 4 | 4 | 600 | 600
M. Baiji | 8 |  |  |  | Gas Oil |  | Musil Dam reg | 4 | 4 | 56 | 60 | 900
Quds | 2 | 2 | 190 | 160 | Gas Oil | 35 trucks | Musil Pumping | 2 | 1 | 110 | 0
Mosil | 12 | 8 | 125 | 150 | 29 | #1 rotor defect; #3 stopped at 1225 power sep prob; #9 rotor defect; #11 prog maint | Haditha Dam | 6 | 4 | 200 | 160 | 600
Dibis | 3 | 2 | 45 | 30 | 31 | #4 rehab | Samarra | 3 | 3 | 54 | 55 | 630
Old Mulla | 12 | 7 | 105 | 128 | 500 | #1 acc gear; #5 synch at 1533; #6 HET; #7 gen vib; #8 vib; #12 needs rehab | Himrin | 2 | 2 | 35 | 21 | 150
New Mulla | 6 | 5 | 150 | 173 | 3.2 | #6 generator defect-prog maint | Hindia | 4 | 4 | 6 | 5 | 140
Taji | 7 | 4 | 55 | 55 | 18 | #3 compressor; #5 excit prob; #6 prog maint; #7 needs rehab | Kufa | 4 | 2 | 1 | 0 | 30
M. Taji | 2 |  |  | 18 | Gas Oil | #2 software |  |  | Total | 1062 | 896
Daura | 4 | 2 | 40 | 30 | 17 | #1 prog maint; #3 needs rehab | System Generation |  | 68744 | MWh
Hilla | 4 | 4 | 64 | 64 | 24 | #5 test | Syrian Line Generation |  | 1442 | MWh
Najaf | 3 | 3 | 110 | 129 | 21 |  | Turkey Line Generation |  | 1916 | MWh
Khor | 4 | 1 | 40 | 80 | Natural Gas | #1, #2 prog maint; #3, #4 stopped at 1557; #3 synch at 2051 | Total Generation |  | 77529 | MWh
Shuaiba | 2 | 1 | 4 | 20 | Natural Gas |  | System Peak Load |  | 3965 | MW
M. Shuaiba | 2 |  |  |  | Natural Gas |  | Syria Peak Load |  | 60 | MW
Petro | 4 | 1 | 10 | 0 | Natural Gas |  | Turkey Peak Load |  | 80 | MW
M. Dibis | 4 | 3 | 9 | 24 | Natural Gas |  | Fixed Gen Peak Load |  | 266 | MW
Mossil East | 5 | 3 | 17 | 0 | Gas Oil |  | Total Peak Load |  | 3371 | MW
Hmam/Zafranya | 7 |  |  |  | Gas Oil |  | Baghdad Load |  | 1230 | MW
Diesel |  |  |  |  | Gas Oil
|  | Total | 1054 | 1186
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
Reporting Peak for 12 APRIL 2004 / Report Date - 13 APRIL 2004
Power transferred from North to Middle 900 MW.
Power transferred from South to Middle - 120 MW.
GOVERNORATE | Peak Load MW | MWH | Average Load MW | Demand Load MW
Baghdad | 1230 | 25028 | 1043 | 1368
Duhok | 80 | 1925 | 80 | 107
Naynawa | 300 | 7593 | 316 | 482
Tamim | 135 | 3110 | 130 | 188
Salah Aldeen | 200 | 4775 | 199 | 249
Anbar | 207 | 4593 | 191 | 242
Dyala | 79 | 2107 | 88 | 138
Babil | 93 | 2457 | 102 | 143
Kirbala | 102 | 2158 | 90 | 90
Najaf | 138 | 2475 | 103 | 118
Kadsya | 75 | 1881 | 78 | 120
Wasit | 50 | 1386 | 58 | 82
Muthana | 45 | 1367 | 57 | 77
Nasirya | 65 | 2156 | 90 | 118
Misan | 47 | 1317 | 55 | 77
Basra | 30 | 5450 | 277 | 279